### MAROOCHY SHIRE COUNCIL PLANNING SCHEME

### POLICY NO. DC1

### WATER SUPPLY & SEWERAGE INFRASTRUCTURE

### DC 1.1	INTRODUCTION

(1)	From an infrastructure planning and charging perspective, the development of the water supply and sewerage infrastructure strategy has been generally based on a number of community outcomes or objectives outlined in the customer services standards for Maroochy Water Services (the commercialised business unit of Council).

(2)	For water supply infrastructure, Maroochy Water Services is to provide water that:

- is a of a quality that maintains the health of the community;

- is clear and free from objectionable odour and taste;

- is reliably supplied to each property within the water service area;

- performs an effective and affordable service in relation to:

      - delivering water to a desirable pressure and flow

      - ensuring fire fighting can be undertaken with the supply

      - optimising the network and operating conditions to reduce whole of life costs and provide an efficient service

- fosters sustainable water consumption, including:

      - ensuring that potable water supply methods are applied in the context of water sensitive urban design

      - managing the collection and use of water on-site

      - allowing for the efficient development of land through innovative use of on-site storage where appropriate.

(3)	For sewerage infrastructure, Maroochy Water Services is to provide sewerage services that:

- effectively and efficiently remove wastewater from premises located within the sewerage service area;

- appropriately treat wastewater to maintain the health of the community and reduce the impact on the natural environment including contaminant and nutrient loading on waterways;

- reduce odours from the sewerage system and improve the amenity of premises;

- perform an effective and affordable service in relation to:

      - Conveying sewage at adequate velocity to limit blockages and detention times

      - Limiting surcharging of the network

      - Reducing whole of life costs

      - Treating wastewater from industry and the community

- ensure wastewater disposal methods (including effluent reuse) are applied in the context of water sensitive urban design.

(4)	Council is committed to ensure that the water supply & sewerage network provides an effective, efficient and quality service to the community.

(5)	This Planning Scheme Policy is the mechanism to partially fund, via developer contributions, the construction of water supply & sewerage trunk infrastructure.

(6)	Infrastructure contributions are to be provided towards the establishment costs incurred or to be incurred in providing existing and future water supply truck infrastructure and sewerage truck infrastructure in accordance with this planning scheme policy.

(7)	The scope of water supply & sewerage infrastructure for which funding is obtained via this planning scheme policy is limited to water supply & sewerage trunk infrastructure.

(8)	This planning scheme policy –

(a)	specifies the methodology for determining contributions for water supply headworks or sewerage headworks;

(b)	specifies the works, structures or equipment determined to be water supply headworks or sewerage headworks.

NOTE DC 1.1 INTERNAL WATER SUPPLY & SEWERAGE INFRASTRUCTURE

- The ‘internal’ water supply & sewerage infrastructure (eg. water supply or sewerage reticulation mains) is the responsibility of the Developer and will be applied as a condition in any development approval.

- For the purpose of clarity it is recorded that the Council is not responsible for the construction or the cost of any part of internal water supply & sewerage infrastructure.

- Infrastructure contributions payable by a Developer pursuant to this Planning Scheme Policy are additional to the ‘internal’ infrastructure that the Developer is required to provide as part of a development.

(9)	The provisions in this planning scheme policy relate to the Infrastructure Contributions for water supply & sewerage trunk infrastructure as follows -

- The existing water supply & sewerage trunk infrastructure (see section DC 1.2);

- The future water supply & sewerage trunk infrastructure (see section DC 1.3);

- The desired standard of service for water supply & sewerage trunk infrastructure (see section DC 1.4);

- The estimated establishment cost of water supply & sewerage trunk infrastructure (see section DC 1.5);

- The estimated establishment cost of water supply & sewerage trunk infrastructure to be funded by the contribution (see section DC 1.6); and

- Infrastructure contributions and calculations (see sections DC 1.7 and Schedule DC 1).

### DC 1.2	EXISTING WATER SUPPLY & SEWERAGE TRUNK INFRASTRUCTURE

NOTE DC 1.2 A

Water Supply

- The Local Government operates an integrated water supply scheme for the Image Flat/Landers Shute Scheme and a localised scheme for the Town of Kenilworth.

- For the Image Flat/Landers Shute Scheme treated water supplied is purchased in bulk from the Caloundra –Maroochy Water Supply Board by agreement, with the remainder being supplied from the Local Government’s own dams and treatment plant at Image Flat.

- For the Kenilworth Scheme water is sourced from bores and a well adjacent to the Mary River and treated at its own treatment plant.

Sewerage

- The Local Government operates the following sewerage schemes -

(a) Maroochydore;

(b) Nambour;

(c) Coolum;

(d) Suncoast;

(e) Yandina;

(f) Kenilworth;

(g) Eumundi.

- The existing water supply trunk infrastructure is generally shown on DC1 Figure 1 including reference to the detailed drawings (refer Appendix 1).

- The existing sewerage trunk infrastructure is generally shown on DC1 Figure 2 including reference to the detailed drawings (refer Appendix 2).

NOTE DC 1.2 B

Further details in relation to existing water supply & sewerage trunk infrastructure, can be found in the ‘Water and Sewerage Network Analysis 2004 including supporting detailed drawings’, that forms part of this planning scheme policy.

### DC 1.3	FUTURE WATER SUPPLY & SEWERAGE TRUNK INFRASTRUCTURE

(1)	The future trunk infrastructure to be provided for—

  - District and zonal water supply trunk infrastructure is generally shown on DC1 Figure 1 including reference to the detailed drawings (refer Appendix 1).

  - District and sub–catchment sewerage trunk infrastructure is generally shown on DC1 Figure 2 including reference to the detailed drawings (refer Appendix 2).

NOTE DC 1.3

Further details in relation to future water supply & sewerage trunk infrastructure, can be found in the ‘Water and Sewerage Network Analysis 2004 including supporting detailed drawings’ that forms part of this planning scheme policy.

DC 1.4	DESIRED STANDARD OF SERVICE FOR WATER SUPPLY & SEWERAGE TRUNK INFRASTRUCTURE

(1)	The desired standard of service for water supply & sewerage trunk infrastructure is outlined in Table DC 1.4.1 (refer Appendix 3).

NOTE DC 1.4

- It is acknowledged that in some cases, due to local circumstances, the desired standard of service may not be met.

- In these situations, water supply & sewerage trunk infrastructure aims to meet the standards to the greatest degree practicable.

### DC 1.5 	ESTIMATED COST OF WATER SUPPLY AND SEWERAGE TRUNK INFRASTRUCTURE

(1)	The estimated establishment costs for water supply & sewerage trunk infrastructure is outlined in Table DC 1.5.

### TABLE DC 1.5 WATER SUPPLY & SEWERAGE TRUNK INFRASTRUCTURE COSTS ($)

| Infrastructure Works | Existing Trunk Infrastructure | Future Trunk Infrastructure | Total |
| --- | --- | --- | --- |
| Water Supply |  |  |  |
| District | $173,065,019 | $283,693,155 | $456,758,175 |
| Zonal | $86,768,044 | $48,743,145 | $135,511,190 |
| Sewerage |  |  |  |
| District | $138,183,123 | $422,026,189 | $560,209,312 |
| Sub-catchment | $106,864,117 | $46,150,050 | $153,014,168 |
| Total | $504,880,304 | $800,612,540 | $1,305,492,844 |

NOTE DC 1.5

- Further details in relation to the estimated establishment costs for future water supply & sewerage trunk infrastructure for the various water supply zones and sewerage sub-catchments can be found in the ‘Water and Sewerage Network Analysis 2004 including supporting detailed drawings’, that forms part of this planning scheme policy.

- Within the water supply and sewerage trunk infrastructure categories, connecting works have not been costed as these works are generally not planned in the overall network analysis.

DC 1.6 	PROPORTION OF WATER SUPPLY & SEWERAGE TRUNK INFRASTRUCTURE ESTABLISHMENT COSTS TO BE FUNDED BY INFRASTRUCTURE CONTRIBUTIONS

(1)  The proportion of water supply & sewerage trunk infrastructure costs attributable to    infrastructure contributions is outlined in Table DC 1.6.

TABLE DC1.6 PROPORTION OF WATER SUPPLY & SEWERAGE TRUNK INFRASTRUCTURE ESTABLISHMENT COSTS SUBJECT TO INFRASTRUCTURE CONTRIBUTIONS ($)

| TYPE OF WORKS | COSTS NOT SUBJECT TO INFRASTRUCTURE CONTRIBUTIONS | COSTS SUBJECT TO INFRASTRUCTURE CONTRIBUTIONS |
| --- | --- | --- |
| WATER SUPPLY DISTRICT WATER SUPPLY ZONAL SEWERAGE DISTRICT SEWERAGE SUB-CATCHMENT | $148,562,113 $48,418,707 $148,634,678 $48,068,396 | $308,196,062 $87,092,482 $411,574,634 $104,945,772 |
| # TOTAL | $393,683,894 | $911,808,950 |

#### DC1.7 	INFRASTRUCTURE CONTRIBUTIONS AND CALCULATIONS

(1)  Those areas of the Shire and the type of development applications subject to water supply and sewerage trunk infrastructure contributions together with the method of calculating the contribution is outlined in Schedule DC 1.

SCHEDULE DC 1: WATER SUPPLY & SEWERAGE TRUNK INFRASTRUCTURE 	CONTRIBUTIONS SCHEDULE

AREAS WHERE INFRASTRUCTURE CONTRIBUTIONS APPLY

(1)  For the purpose of determining infrastructure contributions towards water supply and sewerage trunk infrastructure, water supply and sewerage trunk infrastructure has been generally categorised as outlined in Table 1 —

##### Table 1: Water Supply & Sewerage Trunk Infrastructure Categories

| Infrastructure Category | Area | Type of Work |
| --- | --- | --- |
| Water Supply | District | Dams, water treatment plants, raw water mains to water treatment plants, treated water mains to Council bulk supply points, trunk delivery mains from bulk supply points and water treatment plants, pump stations, reservoirs, associated telemetry systems and monitoring instrumentation. |
| Water Supply | Zonal | Zonal raw water mains and raw water pumping stations (eg Kenilworth), zonal water treatment plants (eg Kenilworth), Distribution mains, elevated and non-District reservoirs, Distribution pump stations, associated telemetry systems and monitoring instrumentation. |
| Sewerage | District | Sewage Treatment Plants, effluent and biosolids reuse and disposal systems, trunk sewers, pressure mains, pump stations, associated telemetry systems, instrumentation and odour control systems. |
| Sewerage | Sub-catchment | Trunk collection sewers and pressure mains, pump stations, associated telemetry systems, instrumentation and odour control systems. |

(2)	Those areas of the Shire that are to be provided with District trunk infrastructure are to be subject to a District trunk infrastructure contribution, which is that part of the Water Supply & Sewerage Trunk Infrastructure Contribution used to provide District facilities.

(3)	Those areas of the Shire that are to be provided with Zonal or Sub-catchment trunk infrastructure are to be subject to a Zonal or Sub-catchment trunk infrastructure contribution, which is that part of the Water Supply & Sewerage Trunk Infrastructure Contribution used to provide respectively Zonal and Sub-catchment facilities.

(4)	Those areas of the Shire subject to trunk infrastructure contributions and the boundaries of the various infrastructure categories are, for water supply zones shown on DC1 Figure 3 (refer Appendix 4) and for sewerage sub-catchments shown on DC1 Figure 4 (refer Appendix 5).

# APPLICATION OF CONTRIBUTION

(5) 	Subject to clause (5A), Water Supply & Sewerage Trunk Infrastructure Contributions apply to every development application that involves –

(a)	Reconfiguring a lot; or

(b)	A material change of use

(5A) The following uses are exempt from paying water supply and sewerage infrastructure

contributions –

(a)	all uses defined within the ‘Rural Use’ category as defined in the Planning Scheme 	(unless a connection to the water supply or sewerage network is required);

(b)	uses defined in the Planning Scheme as ‘Car Park’, ‘Extractive Industry’ (unless a 	connection to the water supply or sewerage network is required) or ‘Home-based 	business’ (provided equivalent demand for a detached house is not exceeded);

(c)	a material change of use for a detached house, except where the lot is not connected to the reticulated water supply or sewerage network or where the lot is not subject to a vacant water supply or sewerage charge.  In this regard, the water supply and sewerage networks are to be treated as separate systems, subject to separate determinations about infrastructure charges; or

(d)	Non-complying Self-Assessable Development as defined in Planning Scheme 	Policy DCA – Administration.

# DETERMINATION OF WATER SUPPLY & SEWERAGE TRUNK INFRASTRUCTURE UNIT RATES

(6)	The Water Supply & Sewerage Trunk Infrastructure Unit Rates for the purposes of calculating Water Supply & Sewerage Trunk Infrastructure Contributions is to be determined for each area in respect of each category of Water Supply & Sewerage trunk infrastructure set out in Table 1.

(7)	The Water Supply & Sewerage Trunk Infrastructure Unit rate has been calculated as follows –

Rate = A + B

Where

A	is the district rate determined by the relevant district establishment costs ÷  equivalent population for the area serviced by the district infrastructure.

B	is the zonal or sub-catchment rate determined by the relevant establishment costs for each applicable zone or sub-catchment ÷ equivalent population for each applicable zone or sub-catchment.

(8)	The water supply & sewerage trunk infrastructure unit rates for the various zones or sub-catchments, based on the calculation in paragraph (7), are contained in Table 3 (Water Supply) and Table 4 (Sewerage).

# DETERMINATION AND CALCULATION OF WATER SUPPLY OR SEWERAGE TRUNK INFRASTRUCTURE CONTRIBUTIONS

(9)	The water supply or sewerage trunk infrastructure contribution for any proposed development is to be calculated as follows –

[(A – B) – C] x D x E

Where

A (being proposed demand) is –

i.	For reconfiguring a lot the water supply or sewerage demand factor for the Land or lots (excluding any Dedicated Lots) included in the development application based on the method creating the higher level of demand calculated using the rates outlined in Table 2 (a) and Table 2 (b).

ii.	For a material change of use the water supply or sewerage demand factor for the use or Land included in the development application based on the method creating the higher level of demand calculated using the rates outlined in Table 2 (a) and Table 2 (b).

iii.	For a material change of use where an existing building or existing work is proposed to be changed or extended or a new building or work is proposed to be erected on land occupied by an existing use the water supply or sewerage demand factor for the use included in the development application calculated using the rates outlined in Table 2 (b).

B	(being existing use demand entitlements) is –

- For vacant land, the water supply or sewerage demand factor allowed for a single detached house (3.2 EP) or where previous infrastructure contributions have been paid to Council the demand on which the previous contributions were based.

- Otherwise, the existing use demand entitlement.

C	is any applicable infrastructure credit for the land (granted as a result of providing advanced funding for the construction of trunk infrastructure or contributing trunk infrastructure) as outlined in the register of Infrastructure Contributions and Credits.

D	is the applicable water supply or sewerage trunk infrastructure unit rate as outlined respectively in Tables 3 or 4 for the zone or sub-catchment in which the land is situated.

E	is the applicable water supply or sewerage trunk infrastructure unit charge at the date of payment (refer to Section 3.5 Infrastructure Unit Charges in Planning Scheme Policy DCA – Administration for details of the water supply or sewerage trunk infrastructure unit charge currently in force).

NOTE 1 SCHEDULE DC 1

UNIT CHARGES

(1)	For convenience, the trunk infrastructure unit charge for water supply trunk infrastructure or sewerage trunk infrastructure is contained in the Local Government’s Scale of Fees and Charges.

NOTE 2 SCHEDULE DC1

EXAMPLES

(1)	(a)	It is proposed to reconfigure 3 hectares of land at Coolum Beach on the 			boundaries of Precincts 4 and 9 into:-

(A): 1 lot (8000m²) for future unspecified shops;

(B): 1 lot (5000m²) for future house sites (unspecified number of lots)				and

(C): 19 residential lots on 1.7 hectares comprising 15 traditional house 				lots and 4 courtyard lots

(b)	No previous water supply contributions were paid nor is the land subject 			to infrastructure credits. The land is subject to a vacant water rate.

(c)	The water supply infrastructure demand for the proposed development 			using the rates outlined in Table 2(a) and Table 2 (b) is as follows:-

C

1.7 ha

As there is a ‘residential lot’ proposal for the land use both Table 2 (a) and Table 2 (b) to determine the demand factor and choose whichever Table calculates the highest demand factor (i.e. EP)

B

5000 m2

As this proposed lot is a ‘Management Lot’ the water supply demand factor is equivalent to a single detached house – refer Table 2(a) or Table 2(b)

A

8000 m2

As this proposed lot is a ‘Management Lot’ the water supply demand factor is equivalent to a single detached house – refer Table 2(a) or Table 2(b)

The demand for a single detached house

= 3.2 EP      

The demand for a single detached house

= 3.2 EP      

30 EP/ha x 1.7 ha

= 51 EP      

OR

15 trad. lots x 3.2 EP

= 48 EP

4 c’yard lots x 3.2 EP

= 12.8 EP

= 60.8 EP           

(d)	The water supply demand for the development (A) = 67.2 EP

(e)	As the land is not subject to infrastructure credits nor the subject of previous water supply contributions but is subject to a vacant water rate the existing demand is that allowed for a single detached house (refer to ‘B’ in the calculation formula).

(f)	The demand for a single detached house is 3.2 EP (refer to ‘B’ in the calculation formula).

B = 3.2EP

(g)	The increase in demand is A – B = 64 EP

(h)	The infrastructure contribution is –

64 x 2,081                 (from Table 3 Zone 12-Coolum Int)

133,184 x $1.0762    (Infrastructure Unit Charge)

=	$143,332.62

(2)	(a)	It is proposed to extend by 500m2 an existing 1000m2 shopping centre at Kuluin / Kunda Park.

(b)	As this is an extension to an existing use infrastructure contributions only apply to the proposed extension.

(c)	No previous water supply contributions were paid nor is the land subject to infrastructure credits.

(d)	The water supply infrastructure demand for the proposed development using the rates outlined in Table 2(b) is as follows:-

Use Table 2 (b) (Defined Uses) to determine the demand factor for a ‘Shopping Complex’.

1500m2     x    1.25 EP

100m2

= 18.75 EP

(e)	The water supply demand for the development (A) = 18.75 EP

(f)	The existing water supply infrastructure demand for the shopping centre is as follows –

1000m2    x     1.25 EP             B = 12.5EP

100m2

(g)	The increase in infrastructure demand is A-B which equals 6.25EP.

(h)	The infrastructure contribution is-

6.25 x 1,538             	(from Table 3 Zone 17 – Kunda)

9,612.50 x $1.0762        (Infrastructure Unit Charge)

= $10,344.97

(3)	(a) 	In this example assume the same parameters as outlined in example (2) 				except that previous contributions of $5,200 were paid for the existing

centre.

(b)	The water supply demand for the development (A) = 18.75 EP

(refer example 2).

(c)	The existing EP demand is to be equal to the EP on which the previous 				payment was determined. It was ascertained that the $5,200 previous 				payment was determined using 5.5 EP. The 5.5 EP becomes the existing 				use demand factor.

(d)	The increase in infrastructure demand is A-B which equals 13.25 EP.

(e)	The infrastructure contribution is –

13.25 x 1,538   	(from Table 3 Zone 17  - Kunda)

20,378.50 x $1.0762	(Infrastructure Unit Charge)

= $21,931.34

(4) 	(a)	It is proposed to demolish an existing fabrication industry workshop (2000m2 GFA) to construct a 2500m2 shopping centre at Kunda Park.

(b)	The land is 8000m2 within the ‘Local Centre’ Precinct.

(c)	No previous water supply contributions were paid nor is the land subject to infrastructure credits.

(d)	The water supply infrastructure demand for the proposed development using the rates outlined in Table 2(a) and Table 2 (b) is as follows -

Use both Table 2(a) and Table 2 (b) to determine the demand factor and choose whichever Table calculates the highest demand factor (i.e. EP)

Using Table 2(a), the demand is:

35 EP / ha  x  8000m2

10000m2

= 28 EP                 

OR

Using Table 2 (b), the demand for a ‘shopping complex’ is:

2500m2   x 1.25 EP

100m2

= 31.25 EP              

(e)	The water supply demand for the development (A) = 31.25 EP.

(f)	The existing water supply infrastructure demand for the fabrication industry (‘General Industry’) is as follows –

2000m2  x 0.75 EP

100m2 	B = 15 EP

(g) 	The increase in infrastructure demand is A – B which equals 16.25 EP.

(h) 	The infrastructure contribution is –

16.25 x 1,538      	(from Table 3 Zone 17 – Kunda)

24,992.50 x $1.0762          (Infrastructure Unit Charge)

= $26,896.93

(5) 	(a)	It is proposed to demolish existing shops (2000m2  GFA) and construct 120 two bedroom dwelling units and 1000m2  shops at Maroochydore.

(b)	The land is 8000 m2 within the ‘Multi-storey Residential’ Precinct.

(c)	No previous water supply contributions were paid nor is the land subject to infrastructure credits.

(d)	The water supply infrastructure demand for the proposed development using the rates outlined in Table 2(a) and Table 2 (b) is as follows:–

Use both Table 2(a) and Table 2 (b) to determine the demand factor and choose whichever Table calculates the highest demand factor (i.e. EP)

Using Table 2 (a), the demand is:

300 EP  x  8000m2

10000 m2

= 240 EP             

OR

Using Table 2 (b), the demand for ‘Multiple Dwelling Units’

(2 bedroom/unit) and ‘Shops’ is:

120 units x 1.5 EP / du    = 180 EP

1000 m2   x 1.25 EP      =    12.5 EP

100 m2

= 192.5 EP             

(e)	The water supply demand for the development (A) = 240 EP.

(f)	The existing water supply infrastructure demand for the shops is as follows –

2000 m2  x  1.25 EP		B = 25 EP

100m2

(g)	The increase in infrastructure demand is A – B which equals 215 EP.

(h)	The infrastructure contribution is –

215 x 1,396       	(from Table 3 Zone 18 – Maroochy South)

300,140 x $1.0762    	(Infrastructure Unit Charge)

= 	$323,010.66

Notes:

EP	=	Equivalent Population

du	=	dwelling unit

GFA	=	Gross Floor Area

ha	=	hectare

Water Supply and Sewerage Demand Factor Rates

(10)	The water supply and sewerage demand factor rates for the various precinct classes within each Planning Area outlined in Volume 3 of this Planning Scheme is shown in Table 2 (a).

(11)	The water supply and sewerage demand factor rates for the various uses outlined in section 3.3 (Use Definitions) Volume 1 of this Planning Scheme are shown in Table 2 (b).

(12)	Where calculating the proposed demand requires the use of both Table 2 (a) and Table 2 (b) for determining the water supply or sewerage demand factor rate, the table that calculates the highest demand factor rate is to be used as the water supply or sewerage demand factor.

Table 2 (a):  Water Supply and Sewerage Demand Factor Rates for 	General or Specific Precincts

| Precinct* | No | Planning Area | Water Supply Demand Factor** |  | Sewerage Demand Factor** |
| --- | --- | --- | --- | --- | --- |
| Business and Industry | All Precincts |  | 25EP/ha |  | 35EP/ha |
| Core Industry | All Precincts |  | 25EP/ha |  | 35EP/ha |
| General Rural Lands | All Precincts |  | N/A |  | N/A |
| Hill slope Residential | All Precincts |  | 15EP/ha |  | 15EP/ha |
| Local Centre | 22 | Maroochydore | 45EP/ha |  | 90EP/ha |
|  | All other precincts |  | 35EP/ha |  | 70EP/ha |
| Master Planned Community | 9 | Maroochydore | 110EP/ha |  | 121EP/ha |
|  | 10 | Maroochydore | 110EP/ha |  | 121EP/ha |
|  | 11 | Maroochydore | 110EP/ha |  | 121EP/ha |
|  | 15 | Maroochydore | 90EP/ha |  | 99EP/ha |
|  | 28 | Nambour | 35EP/ha |  | 38.5EP/ha |
|  | 4 | Sippy Downs | 40EP/ha |  | 44EP/ha |
|  | 5 | Sippy Downs | 40EP/ha |  | 44EP/ha |
|  | 8 | Sippy Downs | 40EP/ha |  | 44EP/ha |
|  | 11 | Sippy Downs | 40EP/ha |  | 44EP/ha |
|  | 15 | North Shore | 30EP/ha |  | 33EP/ha |
|  | 16 | North Shore | 190EP/ha |  | 209EP/ha |
|  | 8 | Mt. Coolum | 100EP/ha |  | 133EP/ha |
|  | 9 | Mt. Coolum | 35EP/ha |  | 38.5EP/ha |
|  | 16 | Eudlo Creek Valley | 50EP/ha |  | 55EP/ha |
|  | All other precincts |  | 30EP/ha |  | 30EP/ha |
| Mixed Housing | 13 | Maroochydore | 135EP/ha |  | 180EP/ha |
|  | 17 | Maroochydore | 120EP/ha |  | 160EP/ha |
|  | 20 | Maroochydore | 120EP/ha |  | 160EP/ha |
|  | 23 | Maroochydore | 110EP/ha |  | 146EP/ha |
|  | 25 | Maroochydore | 135EP/ha |  | 180EP/ha |
|  | 27 | Maroochydore | 120EP/ha |  | 160EP/ha |
|  | 3 | Nambour | 80EP/ha |  | 106EP/ha |
|  | 4 | Nambour | 80EP/ha |  | 106EP/ha |
|  | 7 | Mooloolaba | 135EP/ha |  | 180EP/ha |
|  | 8 | Mooloolaba | 135EP/ha |  | 180EP/ha |
|  | 13 | Mooloolaba | 140EP/ha |  | 186EP/ha |
|  | 2 | Buderim | 85EP/ha |  | 113EP/ha |
|  | 5 | Alexandra Headland/ Cotton Tree | 120EP/ha |  | 160EP/ha |
|  | 8 | Alexandra Headland/ Cotton Tree | 140EP/ha |  | 186EP/ha |
|  | 10 | Alexandra Headland/ Cotton Tree | 120EP/ha |  | 160EP/ha |
|  | 11 | Alexandra Headland/ Cotton Tree | 135EP/ha |  | 180EP/ha |
|  | 4 | Kuluin/Kunda Park | 70EP/ha |  | 93EP/ha |
|  | 13 | North Shore | 70EP/ha |  | 93EP/ha |
|  | 2 | Mt. Coolum | 140EP/ha |  | 186EP/ha |
|  | 3 | Coolum Beach | 200EP/ha |  | 266EP/ha |
|  | 2 | Woombye | 60EP/ha |  | 80EP/ha |
|  | 6 | Eumundi | 60EP/ha |  | 80EP/ha |
|  | All other precincts |  | 100EP/ha |  | 133EP/ha |
| Multi-storey Residential | 5 | Mooloolaba | 240EP/ha |  | 384EP/ha |
|  | 6 | Mooloolaba | 240EP/ha |  | 384EP/ha |
|  | 2 | Alexandra Headland/Cotton Tree | 320EP/ha |  | 512EP/ha |
|  | 2 | North Shore | 200EP/ha |  | 320EP/ha |
|  | All other precincts |  | 300EP/ha |  | 480EP/ha |
| Neighbourhood Residential | All Precincts |  | 30EP/ha |  | 30EP/ha |
| Special Purpose | 3 | Sippy Downs | 150EP/ha |  | 150EP/ha |
|  | All Other Precincts |  | To determine demand factor rates, use the precinct or precincts from this table that most closely align with the proposed development |  | To determine demand factor rates, use the precinct or precincts from this table that most closely align with the proposed development |
| Sustainable Cane Lands | All Precincts |  | N/A |  | N/A |
| Sustainable Horticultural Lands | All Precincts |  | N/A |  | N/A |
| Sustainable Pastoral Lands | All Precincts |  | N/A |  | N/A |
| Sustainable Rural Residential | All Precincts |  | 5EP/ha |  | N/A |
| Town Centre Core | 1 | Maroochydore | 300EP/ha |  | 600EP/ha |
|  | 2 | Maroochydore | 200EP/ha |  | 400EP/ha |
|  | 3 | Maroochydore | 110EP/ha |  | 220EP/ha |
|  | 4 | Maroochydore | 300EP/ha |  | 600EP/ha |
|  | 1 | Nambour | 50EP/ha |  | 100EP/ha |
|  | 1 | Sippy Downs | 60EP/ha |  | 120EP/ha |
|  | 1 | Mooloolaba | 300EP/ha |  | 600EP/ha |
|  | All other precincts |  | 50EP/ha |  | 100EP/ha |
| Town Centre Frame | 5 | Maroochydore | 40EP/ha |  | 80EP/ha |
|  | 6 | Maroochydore | 35EP/ha |  | 70EP/ha |
|  | 7 | Maroochydore | 150EP/ha |  | 300EP/ha |
|  | 8 | Maroochydore | 200EP/ha |  | 400EP/ha |
|  | 2 | Nambour | 45EP/ha |  | 90EP/ha |
|  | 2 | Sippy Downs | 80EP/ha |  | 160EP/ha |
|  | 2 | Mooloolaba | 200EP/ha |  | 400EP/ha |
|  | 3 | Mooloolaba | 200EP/ha |  | 400EP/ha |
|  | 4 | Mooloolaba | 100EP/ha |  | 200EP/ha |
|  | 1 | Kuluin/Kunda Park | 35EP/ha |  | 70EP/ha |
|  | All other precincts |  | 50EP/ha |  | 100EP/ha |
| Village Centre | 1A | Buderim | 45EP/ha | 90EP/ha |  |
|  | 1B | Buderim | 45EP/ha | 90EP/ha |  |
|  | 1 | Coolum Beach | 200EP/ha | 400EP/ha |  |
|  | All other precincts |  | 35EP/ha | 70EP/ha |  |
| Water Resource Catchment Area | All Precincts |  | N/A | N/A |  |

*Where contained in an urban or service area and requires service of the infrastructure network

**For a ‘Management Lot’ the Water Supply Demand Factor and Sewerage Demand Factor is 3.2EP/Lot.

Notes:

EP = Equivalent Person

ha  = hectare

Table 2 (b): Water Supply and Sewerage Demand Factor Rates for Defined Uses*

| Defined Uses and Use Classes | Assessment Unit |  | Water Supply Ep/Unit** | Sewerage Ep/Unit** |
| --- | --- | --- | --- | --- |
| RESIDENTIAL USES |  |  |  |  |
| Accommodation Building | Bed |  | 1.28 | 1.28 |
| Bed and Breakfast | Lettable Room |  | 0.9 | 0.9 |
| Caravan Park | Caravan Site |  | 1.28 | 1.6 |
|  | Relocatable home site |  | 1.72 | 2.52 |
| Caretakers Residence | 1 bedroom |  | 1.44 | 1.92 |
|  | 2 bedroom |  | 1.92 | 2.56 |
|  | 3 or more bedrooms |  | 2.4 | 3.2 |
| Detached House | Lot |  | 3.2 | 3.2 |
| Display Home | As per detached house or dual occupancy or multiple dwelling units, depending on nature of development |  |  |  |
| Dual Occupancy | 1 bedroom |  | 1.44 | 1.92 |
|  | 2 bedroom |  | 1.92 | 2.56 |
|  | 3 or more bedrooms |  | 2.4 | 3.2 |
| Home-Based Business | Lot |  | Exempt provided equivalent demand for a detached house is not exceeded, otherwise to be assessed on use. |  |
| Institutional Residence | Bed |  | 1.28 | 1.28 |
| Integrated Tourist Facility | Bed |  | 1.28 | 1.28 |
|  | For permanent residential accommodation as per detached house or dual occupancy or multiple dwelling units, depending on nature of development. |  |  |  |
| Motel (includes hotel accommodation) | Per unit |  | 1.2 | 1.8 |
| Multiple Dwelling Units | 1 bedroom |  | 0.9 | 1.5 |
|  | 2 bedroom |  | 1.5 | 2.4 |
|  | 3 or more bedrooms |  | 2.0 | 3.2 |
| Residential Care facility |  | Per self contained dwg | 2.0 | 3.2 |
|  |  | Per hostel unit | 1.8 | 2.4 |
|  |  | Per nursing care bed | 1.8 | 1.8 |
| Retirement Village |  | 1 bedroom | 0.9 | 1.5 |
|  |  | 2 bedroom | 1.5 | 2.4 |
|  |  | 3 or more bedrooms | 2.0 | 3.2 |
| RURAL USES |  |  |  |  |
| Agriculture, Animal Keeping, Animal Husbandry, Aquaculture, Forestry, Intensive Animal Husbandry, Roadside stall, Stables |  | Exempt, unless a connection to the water supply or sewerage network is required in which case demand is to be determined by Council assessed on use. |  |  |
| Rural Service Industry |  | Exempt, unless connection to network required then as determined by Council assessed on use |  |  |
| Winery |  |  |  |  |

| Defined Uses and Use Classes |  |  | Assessment Unit | Water Supply Ep/Unit** |  | Sewerage Ep/Unit** |
| --- | --- | --- | --- | --- | --- | --- |
| COMMERCIAL USES |  |  |  |  |  |  |
| Adult Product Shop |  |  | Per 100m2 (GFA) | 1.25 |  | 1.25 |
| Art & Craft Centre |  |  | Per 100m2 (GFA) | 1.25 |  | 1.25 |
| Convenience Restaurant |  |  | Per 100m2 (GFA) | 4.0 |  | 4.0 |
| Fast Food Store |  |  | Per 100m2 (GFA) | 7.5 |  | 7.5 |
| Funeral Parlour |  |  | Per 100m2 (GFA) | 0.5 |  | 0.5 |
| Garden Centre |  |  | Per 100m2 Site area | 0.8 |  | 0.16 |
| Hotel (excluding hotel accommodation) |  |  | Per flushing unit, WC or Urinal | 3.52 |  | 3.52 |
| Market |  |  | As determined by Council |  |  |  |
| Medical Centre |  |  | Per Consultation Room | 0.96 |  | 0.96 |
| Office |  |  | Per 100m2 (GFA) | 1.25 |  | 1.25 |
| Restaurant |  |  | Per 100m2 (GFA) | 4.0 |  | 4.0 |
| Shop (including General Store) |  |  | Per 100m2 (GFA) | 1.25 |  | 1.25 |
| Shopping Complex |  |  | Per 100m2 (GFA) | 1.25 |  | 1.25 |
| Showroom |  |  | Per 100m2 (GFA) | 1.25 |  | 1.25 |
| Veterinary Clinic |  |  | Per 100m2 (GFA) | 1.25 |  | 1.25 |
| INDUSTRIAL USES |  |  |  |  |  |  |
| Car Washing Station |  |  | Per wash bay | 8.0 |  | 11.84 |
| Environmentally Assessable Industry |  |  | Per 100m2 (GFA) | 0.75 |  | 0.75 |
| Extractive Industry |  |  | Exempt, unless connection to network required then as determined by Council |  |  |  |
| General Industry |  |  | Per 100m2 (GFA) | 0.75 |  | 0.75 |
| Landscape Supplies |  |  | As determined by Council |  |  |  |
| Light Industry | Laundromat |  | Per 100m2 (GFA) | 19.2 |  | 28.8 |
|  | Hot bread kitchen/retail bakery |  | Per 100m2 (GFA) | 0.75 |  | 0.75 |
|  | All other uses |  | Per 100m2 (GFA) | 0.75 |  | 0.75 |
| Sales or Hire Yard |  |  | As determined by Council |  |  |  |
| Service Station |  |  | Per lot | 6.4 |  | 6.4 |
| Storage Yard |  |  | As determined by Council |  |  |  |
| Transport Station |  |  | As determined by Council |  |  |  |
| Vehicle Depot |  |  | As determined by Council |  |  |  |
| Vehicle Repair workshop |  |  | Per 100m2 (GFA) | 0.75 |  | 0.75 |
| Warehouse |  |  |  | Per 100m2 (GFA) | 0.25 | 0.25 |
| OTHER USES |  |  |  |  |  |  |
| COMMUNITY USE |  | Child Care Centre |  | Staff/pupil | 0.15 | 0.15 |
|  |  | Local Utility |  |  | As determined by Council |  |
|  |  | Major Utility |  |  | As determined by Council |  |
|  |  | Telecommunications Facility |  |  | As determined by Council |  |
| SPECIAL USE |  | Cemetery |  |  | As determined by Council |  |
|  |  | Church |  | Per 100m2 (GFA) | 6.4 | 9.6 |
|  |  | Community Meeting Hall |  | Per 100m2 (GFA) | 5.12 | 5.12 |
|  |  | Crematorium |  | Per 100m2 (GFA) | 1.25 | 1.25 |
|  |  | Educational Establishment |  | Per enrolment | 0.15(1) | 0.25(1) |
|  |  | Emergency Services |  |  | As determined by Council |  |
|  |  | Hospital |  | Bed | 2.4 | 2.4 |

| Defined Uses and Use Classes |  |  | Assessment Unit | Water Supply Ep/Unit** | Sewerage Ep/Unit** |
| --- | --- | --- | --- | --- | --- |
| RECREAT– IONAL USES | INDOOR RECREATION | Amusement Centres | per flushing unit, WC or Urinal | 1.175 | 1.175 |
|  |  | Gyms | per flushing unit, WC or Urinal | 1.175 | 1.175 |
|  |  | Indoor Sports Centre | per flushing unit, WC or Urinal | 1.175 | 1.175 |
|  |  | Licensed Club | per flushing unit, WC or Urinal | 3.52 | 3.52 |
|  |  | Unlicensed Club | per flushing unit, WC or Urinal | 1.175 | 1.175 |
|  |  | Night Club | per flushing unit, WC or Urinal | 3.52 | 3.52 |
|  |  | Theatre / Cinema | per flushing unit, WC or Urinal | 3.52 | 3.52 |
|  |  | All other uses | As determined by Council |  |  |
|  | OUTDOOR RECREATION |  | As determined by Council |  |  |
| OTHER USES | CAR PARK |  |  | Exempt | Exempt |

(1) For boarding schools add an additional 1.28ep per bed.

*These rates do not apply to water intensive establishments that are likely to significantly exceed the specified Ep/Unit rate.  For water intensive establishments, an individual Ep/Unit rate is to be calculated based on the anticipated actual water usage or effluent discharge.  Also, the local government may approve a lower estimated demand rate than the specified Ep/Unit rate where it can be demonstrated that water saving/recycling initiatives can be sustainably integrated into a development.

** For a ‘Management Lot’ the Water Supply Ep/Unit and Sewerage Ep/Unit is 3.2 EP/Lot.

Schedule of Infrastructure Unit Rates

(13)	The water supply and sewerage infrastructure unit rates for the various water supply zones (refer Figure 3) or sewerage sub-catchments (refer Figure 4) are shown in the following Tables for water supply (Table 3) or sewerage (Table 4).

TABLE 3:  Schedule of Water Supply Trunk Infrastructure Unit Rates

| Zonal Name | Zone Number | District (Per EP) | Zonal (Per EP) | Infrastructure Unit Rate per Equivalent Person (EP) |
| --- | --- | --- | --- | --- |
| Atkinson Rd | 01 | 1,849 | 2,532 | 4,380 |
| Bli Bli | 02 | 1,636 | 234 | 1,870 |
| BT1 / Pringle R | 03 | 869 | 0 | 869 |
| Buderim - H | 04 | 1,384 | 323 | 1,707 |
| Buderim - Int | 05 | 1,439 | 406 | 1,845 |
| Buderim - LL | 06 | 1,599 | 584 | 2,183 |
| Cathedral | 07 | 1,413 | 414 | 1,827 |
| Coes Creek | 08 | 1,184 | 297 | 1,481 |
| Coolum | 09 | 1,627 | 330 | 1,958 |
| Coolum - H | 10 | 1,588 | 648 | 2,236 |
| Coolum - Ind | 11 | 1,746 | 201 | 1,946 |
| Coolum - Int | 12 | 1,677 | 404 | 2,081 |
| Craigs Hill | 13 | 941 | 586 | 1,527 |
| Eumundi | 14 | 1,823 | 415 | 2,238 |
| Harbour Hill | 15 | 1,070 | 494 | 1,564 |
| Kiel Mountain W | 16 | 1,044 | 2,690 | 3,733 |
| Kunda | 17 | 926 | 612 | 1,538 |
| Maroochy South | 18 | 992 | 404 | 1,396 |
| Mountain Creek | 19 | 1,268 | 294 | 1,562 |
| Nambour West | 20 | 1,057 | 455 | 1,512 |
| North Arm | 21 | 1,501 | 2,880 | 4,381 |
| Panorama | 22 | 1,037 | 525 | 1,563 |
| Peregian | 23 | 1,891 | 304 | 2,196 |
| Pringle Hill | 24 | 1,288 | 198 | 1,486 |
| Rosemount | 25 | 1,210 | 3,731 | 4,941 |
| Sippy Downs | 26 | 795 | 125 | 920 |
| Woombye | 27 | 1,419 | 604 | 2,023 |
| Yandina - H | 28 | 1,190 | 620 | 1,810 |
| Yandina - L | 29 | 1,574 | 325 | 1,899 |
| Yandina - S1 | 30 | 1,493 | 321 | 1,814 |
| Yandina - S2 | 31 | 1,298 | 88 | 1,386 |
| Kenilworth Scheme | 32 | - | 692 | 692 |

TABLE 4:  Schedule of Sewerage Trunk Infrastructure Unit Rates

| Catchment | District (Per EP) | Sub-Catchment (Per EP) | Infrastructure Unit Rate per Equivalent Person (EP) |
| --- | --- | --- | --- |
| Sub-catchment (M01) | 1,131 | 164 | 1,295 |
| Sub-catchment (M02) | 1,213 | 294 | 1,506 |
| Sub-catchment (M03) | 1,367 | 410 | 1,777 |
| Sub-catchment (M04) | 1,172 | 116 | 1,288 |
| Sub-catchment (M05) | 1,262 | 392 | 1,654 |
| Sub-catchment (M06) | 1,387 | 690 | 2,077 |
| Sub-catchment (M07) | 1,394 | 111 | 1,505 |
| Sub-catchment (M08) | 1,441 | 216 | 1,657 |
| Sub-catchment (M09) | 1,441 | 192 | 1,633 |
| Sub-catchment (M10) | 1,092 | 461 | 1,553 |
| Sub-catchment (M11) | 1,089 | 266 | 1,356 |
| Sub-catchment (M12) | 1,195 | 385 | 1,580 |
| Sub-catchment (M13) | 1,373 | 157 | 1,530 |
| Sub-catchment (M14) | 1,402 | 802 | 2,204 |
| Sub-catchment (M15) | 1,064 | 1,273 | 2,336 |
| Sub-catchment (N01) | 1,134 | 800 | 1,935 |
| Sub-catchment (N02) | 1,196 | 290 | 1,486 |
| Sub-catchment (N03) | 1,294 | 324 | 1,618 |
| Sub-catchment (N04) | 1,294 | 524 | 1,818 |
| Sub-catchment (N05) | 1,581 | 367 | 1,948 |
| Sub-catchment (N06) | 1,590 | 727 | 2,317 |
| Sub-catchment (N07) | 1,188 | 458 | 1,646 |
| Sub-catchment (N08) | 1,025 | 637 | 1,662 |
| Eumundi (N09) | 1,669 | 1,314 | 2,983 |
| Yandina (N10) | 1,862 | 551 | 2,413 |
| Sub-catchment (C01) | 1,200 | 434 | 1,634 |
| Sub-catchment (C02) | 1,293 | 374 | 1,667 |
| Sub-catchment (C03) | 1,298 | 251 | 1,549 |
| Sub-catchment (C04) | 1,442 | 489 | 1,930 |
| Sub-catchment (C05) | 1,442 | 877 | 2,318 |
| Sub-catchment (C06) | 1,541 | 89 | 1,629 |
| Sub-catchment (C07) | 1,693 | 309 | 2,003 |
| Sub-catchment (S01) | 1,304 | 296 | 1,600 |
| Sub-catchment (S02) | 1,179 | 759 | 1,939 |
| Sub-catchment (S03) | 1,084 | 859 | 1,943 |
| Sub-catchment (S04) | 1,207 | 371 | 1,579 |
| Kenilworth (K01) | 2,155 | 2,000 | 4,156 |

APPENDIX 1

DC1 FIGURE 1. WATER SUPPLY TRUNK INFRASTRUCTURE

DC1 Figure 1 Water Supply Trunk Infrastructure generally shows the existing and future water supply trunk infrastructure and has been compiled from the following Drawings –

| Drawing No. | Title | Date |
| --- | --- | --- |
| 2838/12/01 – WA | Overall Key Layout Plan | 03-05-2005 |
| 2838/12/01 – WB | Layout Plan – Eumundi and North Arm Districts | 03-05-2005 |
| 2838/12/01 – WD | Layout Plan – Peregian District | 03-05-2005 |
| 2838/12/01 – WE | Layout Plan – North Arm and Yandina Districts | 03-05-2005 |
| 2838/12/01 – WF | Layout Plan – Coolum District | 03-05-2005 |
| 2838/12/01 – WG | Layout Plan – Coolum District | 03-05-2005 |
| 2838/12/01 – WH | Layout Plan – Yandina and Nambour Districts | 03-05-2005 |
| 2838/12/01 – WJ | Layout Plan – Atkinson Road and Bli Bli Districts | 03-05-2005 |
| 2838/12/01 – WK | Layout Plan – Coolum District | 03-05-2005 |
| 2838/12/01 – WL | Layout Plan – Nambour District | 03-05-2005 |
| 2838/12/01 – WM | Layout Plan – Bli Bli, Keil Mountain and Coolum Districts | 03-05-2005 |
| 2838/12/01 – WN | Layout Plan – Coolum and Maroochydore Districts | 03-05-2005 |
| 2838/12/01 – WP | Layout Plan – Woombye and Nambour Districts | 03-05-2005 |
| 2838/12/01 – WQ | Layout Plan – Keil Mountain and Buderim Districts | 03-05-2005 |
| 2838/12/01 – WR | Layout Plan – Maroochydore and Buderim Districts | 03-05-2005 |
| 2838/12/01 – WS | Layout Plan – Landers Shute and Eudlo Districts | 03-05-2005 |
| 2838/12/01 – WT | Layout Plan – Sippy Downs District | 03-05-2005 |
| 2838/12/01 – WU | Layout Plan – Sippy Downs District | 03-05-2005 |
| 2838/12/01 – WV | Layout Plan – Kenilworth District | 03-05-2005 |
| 2838/12/01 – WX | Layout Plan – Yandina and Nambour Districts | 03-05-2005 |

The abovementioned drawings, whilst part of this planning scheme policy, have been collated separately from this document for ease of use.  These drawings are available from the Council.

APPENDIX 2

DC1 FIGURE 2. SEWERAGE TRUNK INFRASTRUCTURE

DC1 Figure 2 Sewerage Trunk Infrastructure generally shows the existing and future sewerage trunk infrastructure and has been compiled from the following Drawings –

| Drawing No. | Title | Date |
| --- | --- | --- |
| 2838/12/01 – SA | Key Plan | 03-05-2005 |
| 2838/12/01 – SB | Eumundi Sewerage Catchment | 03-05-2005 |
| 2838/12/01 – SC | Yandina Sewerage Catchment | 03-05-2005 |
| 2838/12/01 – SD | Nambour Sewerage Catchment | 03-05-2005 |
| 2838/12/01 – SE | Nambour Sewerage Catchment | 03-05-2005 |
| 2838/12/01 – SF | Nambour Sewerage Catchment | 03-05-2005 |
| 2838/12/01 – SG | Coolum Sewerage Catchment | 03-05-2005 |
| 2838/12/01 – SH | Coolum Sewerage Catchment | 03-05-2005 |
| 2838/12/01 – SJ | Suncoast Sewerage Catchment | 03-05-2005 |
| 2838/12/01 – SK | Maroochydore Sewerage Catchment | 03-05-2005 |
| 2838/12/01 – SL | Maroochydore Sewerage Catchment | 03-05-2005 |
| 2838/12/01 – SM | Maroochydore Sewerage Catchment | 03-05-2005 |
| 2838/12/01 – SN | Maroochydore Sewerage Catchment | 03-05-2005 |
| 2838/12/01 – SP | Maroochydore Sewerage Catchment | 03-05-2005 |
| 2838/12/01 – SQ | Kenilworth Sewerage Catchment | 03-05-2005 |

The abovementioned drawings, whilst part of this planning scheme policy, have been collated separately from this document for ease of use.  These drawings are available from the Council.

APPENDIX 3 WATER SUPPLY AND SEWERAGE DESIRED STANDARDS OF SERVICE

TABLE DC 1.4.1

| Water Supply | Sewerage |
| --- | --- |
| - Provide a service of potable water that meets the performance standards outlined in the Australian Drinking Water Guidelines (1996) issued by the National Health and Medical Research Council (NHMRC) | - Provide a service of sanitary drainage that meets the Environmental Protection Authority (EPA) requirements with respect to the containment of sewage and effluent disposal. |
| - Design of the water supply network is to comply with established codes and standards including: - Water Services Association of Australia Code for Water Supply - Queensland Water Resources Commission “Guidelines for Planning and Design of Urban Water Supply Schemes” - Water Act 2000 (N.B. Community expectations should be reflected where codes or standards can be interpreted to the contrary) | - Design of the sewerage network is to comply with established codes and standards including: - Water Services Association of Australia Code for Sewerage Services - Queensland Water Resources Commission “Guidelines for Planning and Design of Sewerage Schemes” - Water Act 2000 and the Plumbing and Drainage Act 2002 - EPA approval conditions and standards (N.B. Community expectations should be reflected where codes or standards can be interpreted to the contrary) |
| - The water supply distribution system is to be designed generally in accordance with State Government Guidelines with: - The minimum pressure expectation at a property boundary being 22 metres head - Average Day Demand (AD) = 370L/EP/day - Design of any non-conventional system will reflect the precepts of the Queensland Water Recycling Strategy and best appropriate practices that achieve the desired outcomes for the potable water supply. | - The sewerage system is to be designed generally in accordance with State Government Guidelines and requirements with: - For gravity sewers a per capita flow based on Average Dry Weather Flow (ADWF) = 225L/EP/day |

APPENDIX 4

#### DC1 Figure 3. Water Supply Zonal Headworks Areas

APPENDIX 5

DC1 FIGURE 4. Sewerage Sub-Catchment Headworks Areas

For water supply and sewerage trunk infrastructure contributions, any equivalent population (EP) for a single detached house only applies where the lot or dwelling is already connected to the reticulated water supply or sewerage network or where the lot is subject to a vacant water supply or sewerage charge.  In this regard the water supply and sewerage networks are to be treated as separate systems, subject to separate determinations about infrastructure.

The onus is upon the applicant to provide evidence of any previous infrastructure contributions paid to Council.

Refer to Division 10 – Glossary of Terms in Planning Scheme Policy DCA – Administration for an explanation of the term “existing use demand entitlement”.